DELEGATED APPLICATION REPORT			Target Date: 31/10/17

Application No: 171496/FUL

Address: 164-168 Whitley Wood Road

Proposal: Installation of replacement plant

Case Officer: Tom Hughes

Site Description and Surrounding Area

The application site is a ground floor retail unit (Class A1), within a parade of shops comprising Whitley Wood local centre.  Mechanical plant, goods entrances, storage and stepped access to the residential accommodation above are located at the rear of the unit. A private car park is located beyond. The surrounding area is predominantly residential.

Proposal

The proposal is for the installation of replacement and additional plant, to be located within the existing plant area at the rear of the retail unit. The proposed plant comprises five compressors, one condenser, one air conditioning unit and one receiver.

Plans Considered

The agent supplied the following, received on 29th August 2017:

Drawing No: 6282(P)100 – Site Location

Drawing No: 6282(P)102 – Existing Site Plan

Drawing No: 6282(P)103 – Proposed Site Plan

Drawing No: WHITLEYWOOD-P1 – Proposed Fixture Layout

Drawing No: CR1 – Proposed Refrigeration Layout

Drawing No: CR2 – Proposed Services and Condensate Layout

Drawing No: CR3 – Proposed Refrigeration Plant Layout

Drawing No: CR4-HT – Refrigeration Schematic

Drawing No: CR4-LT – Refrigeration Schematic

Refrigeration Scope of Works

Subsequently, the agent supplied the following, received on 24th October 2017:

Noise Impact Assessment v.1.2

Relevant Planning History

171045/FUL – Shop front alterations and various external alterations – Permitted 23/08/17

Consultation Responses

Environmental Protection provided the following consultation response:

“The noise assessment submitted has been carried out in accordance with BS4142:2014 and the methodology has been correctly applied, however the assessment concludes that the noise rating level of the proposed plant will be less than -10dB below the background noise so there may be some adverse impact on the local noise climate.

Our draft noise policy states for proposed new plant:

The noise source specific noise level (plant noise level) should be at least 10dBA below the existing background level as measured at the nearest noise sensitive receptor and the rating level should not exceed the background level (as measured in accordance with BS4142:2014).

Within Reading there is strong justification for requiring the plant specific noise level to be at least -10dB below the measured background level. Specifically to prevent cumulative impact from addition of plant over time which could result in background creeping up to levels which might cause adverse health impact, which is more likely in a densely occupied town such as Reading. Levels of -10dB ensure that the background level is not increased and nuisance is unlikely.

However, there may be some situations where this cannot be achieved there may be some flexibility where this is justifiable for example where there are very low background noise levels, etc.

The noise assessment has failed to provide adequate justification for failing to achieve -10dB and therefore I recommend refusal, unless the applicant is able to amend the proposal to reduce sound levels to meet our criteria and provide an updated noise assessment or provide detailed justification as to why it cannot be met, before determination of application.”

The agent subsequently supplied an amended noise assessment. Environmental Protection confirmed that amendment overcomes the concern raised and as such there are no objections to the proposal.

Neighbouring owners and occupiers at 168a and 168b and 181-191 (odd) Whitley Wood Road and 536-540, 538a, 538b and 542 Northumberland Avenue were consulted by letter. No letters of representation were received.

Equality Act 2010

In determining this application, the Council is required to have regard to its obligations under the Equality Act 2010. However, there is no indication or evidence (including from consultation on the application) that the protected groups identified by the Act have or will have different needs, experiences, issues and priorities in relation to this particular planning application. Therefore in terms of the key equalities protected characteristics it is considered there would be no significant adverse impacts as a result of the development.

Relevant Planning Policy and Guidance

The following local and national planning policy and guidance is relevant to this application:

Reading Borough Local Development Framework Core Strategy (2008)

CS7: Design and the Public Realm

CS34: Pollution and Water Resources

Sites and Detailed Policies Document (2012)

SD1: Presumption in Favour of Sustainable Development

DM4: Safeguarding Amenity

Appraisal

The main issues to be considered are:

- Design and impact on the character of the surrounding area

- Impact on neighbours

a) Design and impact on the character of the surrounding area

The proposed plant units will be located within an enclosed plant area at the rear of the building. A number of other plant units are already positioned in this area. The proposed units will be largely hidden from public view and are of a standard unit design. The units are therefore acceptable and are not considered harmful to the character of the building or the surrounding area. As such, they accord with Core Strategy Policy CS7: Design and the Public Realm.

b) Impact on neighbours

As established in the amended noise assessment, the proposed plant would result in the noise source specific noise level (plant noise level) being be at least 10dBA below the existing background level as measured at the nearest noise sensitive receptor. The rating level would not exceed the background level (as measured in accordance with BS4142:2014). The proposal is therefore in accordance with Core Strategy Policy CS34: Pollution and Water Resources and DM4: Safeguarding Amenity of the Sites and Detailed Policies Document.

Conclusion

The proposed plant units have been assessed and found to be acceptable as they comply with the identified policies.

RECOMMENDATION

GRANT