AIR SOURCE HEAT PUMP: ADDITIONAL DATA

It’s no overly clearly what they’re looking for, or where their measurement/assessment point is. Generally planners want to ensure that the heat pump system passes the noise assessment at the nearest neighbouring window. I have done the calcs based on a 10m distance between the heat pumps and the neighbouring window (see below and attached) – this passes the MCS requirements.

I have attached the calcs themselves (see tab MCS 020) so you can tweak them if you need to.

In terms of assessing the sound itself, where we have 3 heat pumps, it get slightly more complex. Sound (dB) isn’t linear (i.e. it doesn’t increase in a straight line). We use the below link to assess the starting level of the sound:

https://www.noisemeters.co.uk/apps/db-calculator/

We have installed the following on site:

- Mitsubishi EcoDan 11.2kW          60dBA

- Mitsubishi EcoDan 8.5kW             58dBA

- Mitsubishi EcoDan 8.5kW             58dBa

Using the above dB Calculator link, the total comes to 63.5dB

| ASHP - Sound Power Level. |  |  |
| --- | --- | --- |
| 1. Sound power level (dB) |  |  |  |  |  | 63.5 |  |  |
| 2. Sound pressure level (dB) |  |  |  |  |  | Q8 - "Three Reflective Surfaces" |  |  |
| 3.Distance from heat pump to assessment position (meters) |  |  |  |  |  | 10 |  |  |
| 4. dB Distance Reduction |  |  |  |  |  | -22 |  |  |
| 5. Barriers Between heat pump and assessment position |  |  |  |  |  | Barrier (partial view) |  |  |
| 6.Sound pressure level @ assessment position |  |  |  |  |  | 36.5 |  |  |
| 7. Background noise level (dB) |  |  |  |  |  | 40 |  |  |
| 8. Differential between 6. & 7. |  |  |  |  |  | 3.5 |  |  |
| 9. Decibel Correction (dB) |  |  |  |  |  | 41.8 |  |  |
| 10. Final Result (dB) |  |  |  |  |  | 42.0 |  |  |
|  |  |  |  |  |  | Pass |  |  |