## Overheating summary
CIBSE TM59: Design methodology for the assessment of overheating risk in homes
|  | Results file name: | Iteration 7 260515 DSY1.aps
|  | Summer Elevated Air Speed: | 0.1m/s
|  | Occupant category: | Category II (normal)
CIBSE TM59 overheating methodology for predominately nat vent rooms assesses against two criteria, (a) and (b) (for Category 1 occupancy criterion A Tmax is reduced by 1 ⁰K):
- Criterion (a) states that for living rooms, kitchens and bedrooms, the number of hours during which ΔT is greater than or equal to 1⁰K from May to September (or November to March for southern hemisphere locations) shall not exceed 3% of occupied hours.
- Criterion (b) states that the operative temperature of the bedrooms from 22:00-07:00 shall not exceed 26⁰C for more than 1% of annual hours (33 hours is therefore recorded as a fail).
CIBSE TM59 overheating methodology for predominately mech vent rooms states the operative temperature of all rooms shall not exceed 26⁰C for more than 3% of annual occupied hours.
TM59 also states that the inclusion of corridors in the overheating analysis is mandatory where community heating pipework runs through them.
While there is no mandatory target for communal corridors, if an operative temperature of 28⁰C is exceeded for more than 3% of the total annual hours this should be identified as a significant risk.
Natvent room name | Natvent criterion (a) result | Natvent criterion (b) result | Pass/Fail | Mechvent room name | Pass/Fail | Corridor name | Significant overheating risk?
Block A 301 LKD | Pass | NA | Pass | No mech vent rooms to be analysed | NA | Block A L3 Corridor 1 | Yes
Block A 301 Bedroom 1 | Pass | Pass | Pass |  |  | Block A L3 Lobby 1 | Yes
Block A 301 Bedroom 2 | Pass | Pass | Pass |  |  | Block A L3 Lobby 2 | Yes
Block A 302 LKD | Pass | NA | Pass |  |  | Block A L3 Lobby 3 | Yes
Block A 302 Bedroom 1 | Pass | Pass | Pass |  |  | Block A L3 Corridor 3 | Yes
Block A 302 Bedroom 2 | Pass | Pass | Pass |  |  | Block A L3 Corridor 5 | Yes
Block A 303 Bedroom | Pass | Pass | Pass |  |  | Block A L3 Lobby 4 | Yes
Block A 303 LKD | Pass | NA | Pass |  |  | Block A L3 Lobby 5 | Yes
Block A 305 LKD | Pass | NA | Pass |  |  | Block B L3 Lobby 1 | Yes
Block A 305 Bedroom 1 | Pass | Pass | Pass |  |  | Block B L3 Lobby 2 | Yes
Block A 305 Bedroom 2 | Pass | Pass | Pass |  |  | Block B L3 Corridor 2 | Yes
Block A 305 Bedroom 3 | Pass | Pass | Pass |  |  | Block B L3 Corridor 1 | Yes
Block A 306 Bedroom | Pass | Pass | Pass |  |  | Block A L5 Corridor 1 | Yes
Block A 306 LKD | Pass | NA | Pass |  |  | Block A L5 Lobby 1 | Yes
Block A 307 Bedroom | Pass | Pass | Pass |  |  | Block A L5 Lobby 2 | Yes
Block A 307 LKD | Pass | NA | Pass |  |  | Block A L5 Corridor 5 | Yes
Block A 308 LKD | Pass | NA | Pass |  |  | Block A L5 Lobby 4 | Yes
Block A 308 Bedroom | Pass | Pass | Pass |  |  | Block A L5 Lobby 5 | Yes
Block A 310 Bedroom 1 | Pass | Pass | Pass |  |  | Block B L5 Lobby 1 | Yes
Block A 310 Bedroom 2 | Pass | Pass | Pass |  |  | Block B L5 Lobby 2 | Yes
Block A 310 LKD | Pass | NA | Pass |  |  | Block B L5 Corridor 2 | Yes
Block A 311 LKD | Pass | NA | Pass |  |  | Block B L5 Corridor 1 | Yes
Block A 311 Bedroom | Pass | Pass | Pass |  |  | Block B L11 Lobby 1 | Yes
Block A 320 Bedroom | Pass | Pass | Pass |  |  | Block B L11 Lobby 2 | Yes
Block A 320 LKD | Pass | NA | Pass |  |  | Block B L11 Corridor 2 | Yes
Block A 312 Bedroom 1 | Pass | Pass | Pass |  |  | Block B L11 Corridor 1 | Yes
Block A 312 LKD | Pass | NA | Pass |  |  | Block A L3 Corridor 2 | Yes
Block A 312 Bedroom 2 | Pass | Pass | Pass
Block A 313 LKD | Pass | NA | Pass
Block A 313 Bedroom | Pass | Pass | Pass
Block A 315 Bedroom 1 | Pass | Pass | Pass
Block A 315 Bedroom 2 | Pass | Pass | Pass
Block A 315 LKD | Pass | NA | Pass
Block A 316 LKD | Pass | NA | Pass
Block A 316 Bedroom | Pass | Pass | Pass
Block A 317 LKD | Pass | NA | Pass
Block A 317 Bedroom | Pass | Pass | Pass
Block A 318 Bedroom 1 | Pass | Pass | Pass
Block A 318 Bedroom 2 | Pass | Pass | Pass
Block A 318 LKD | Pass | NA | Pass
Block A 319 Bedroom 1 | Pass | Pass | Pass
Block A 319 Bedroom 2 | Pass | Pass | Pass
Block A 319 LKD | Pass | NA | Pass
Block B 301 LKD | Pass | NA | Pass
Block B 301 Bedroom | Pass | Pass | Pass
Block B 302 LKD | Pass | NA | Pass
Block B 302 Bedroom 1 | Pass | Pass | Pass
Block B 302 Bedroom 2 | Pass | Pass | Pass
Block B 303 LKD | Pass | NA | Pass
Block B 303 Bedroom 1 | Pass | Pass | Pass
Block B 303 Bedroom 2 | Pass | Pass | Pass
Block B 304 Bedroom | Pass | Pass | Pass
Block B 306 Bedroom 1 | Pass | Pass | Pass
Block B 306 Bedroom 2 | Pass | Pass | Pass
Block B 306 LKD | Pass | NA | Pass
Block B 304 LKD | Pass | NA | Pass
Block B 305 Studio | Pass | Pass | Pass
Block B 307 Bedroom | Pass | Pass | Pass
Block B 307 LKD | Pass | NA | Pass
Block A 501 LKD | Pass | NA | Pass
Block A 501 Bedroom 1 | Pass | Pass | Pass
Block A 501 Bedroom 2 | Pass | Pass | Pass
Block A 502 LKD | Pass | NA | Pass
Block A 502 Bedroom 1 | Pass | Pass | Pass
Block A 502 Bedroom 2 | Pass | Pass | Pass
Block A 503 Bedroom | Pass | Pass | Pass
Block A 503 LKD | Pass | NA | Pass
Block A 505 LKD | Pass | NA | Pass
Block A 505 Bedroom 1 | Pass | Pass | Pass
Block A 505 Bedroom 2 | Pass | Pass | Pass
Block A 505 Bedroom 3 | Pass | Pass | Pass
Block A 506 Bedroom | Pass | Pass | Pass
Block A 506 LKD | Pass | NA | Pass
Block A 507 Bedroom | Pass | Pass | Pass
Block A 507 LKD | Pass | NA | Pass
Block A 508 LKD | Pass | NA | Pass
Block A 508 Bedroom | Pass | Pass | Pass
Block A 515 Bedroom 1 | Pass | Pass | Pass
Block A 515 Bedroom 2 | Pass | Pass | Pass
Block A 516 LKD | Pass | NA | Pass
Block A 516 Bedroom | Pass | Pass | Pass
Block A 517 LKD | Pass | NA | Pass
Block A 517 Bedroom | Pass | Pass | Pass
Block A 518 Bedroom 1 | Pass | Pass | Pass
Block A 518 Bedroom 2 | Pass | Pass | Pass
Block A 518 LKD | Pass | NA | Pass
Block A 519 Bedroom 1 | Pass | Pass | Pass
Block A 519 Bedroom 2 | Pass | Pass | Pass
Block A 519 LKD | Pass | NA | Pass
Block B 501 LKD | Pass | NA | Pass
Block B 501 Bedroom | Pass | Pass | Pass
Block B 502 LKD | Pass | NA | Pass
Block B 502 Bedroom 1 | Pass | Pass | Pass
Block B 502 Bedroom 2 | Pass | Pass | Pass
Block B 503 LKD | Pass | NA | Pass
Block B 503 Bedroom 1 | Pass | Pass | Pass
Block B 503 Bedroom 2 | Pass | Pass | Pass
Block B 504 Bedroom | Pass | Pass | Pass
Block B 506 Bedroom 1 | Pass | Pass | Pass
Block B 506 Bedroom 2 | Pass | Pass | Pass
Block B 506 LKD | Pass | NA | Pass
Block B 504 LKD | Pass | NA | Pass
Block B 505 Studio | Pass | Pass | Pass
Block B 507 Bedroom | Pass | Pass | Pass
Block B 507 LKD | Pass | NA | Pass
Block A 515 LKD | Pass | NA | Pass
Block B 1101 LKD | Pass | NA | Pass
Block B 1101 Bedroom | Pass | Pass | Pass
Block B 1102 LKD | Pass | NA | Pass
Block B 1102 Bedroom 1 | Pass | Pass | Pass
Block B 1102 Bedroom 2 | Pass | Pass | Pass
Block B 1103 LKD | Pass | NA | Pass
Block B 1103 Bedroom 1 | Pass | Pass | Pass
Block B 1103 Bedroom 2 | Pass | Pass | Pass
Block B 1104 Bedroom | Pass | Pass | Pass
Block B 1106 Bedroom 1 | Pass | Pass | Pass
Block B 1106 Bedroom 2 | Pass | Pass | Pass
Block B 1106 LKD | Pass | NA | Pass
Block B 1104 LKD | Pass | NA | Pass
Block B 1105 Studio | Pass | Pass | Pass
Block B 1107 Bedroom | Pass | Pass | Pass
Block B 1107 LKD | Pass | NA | Pass
Block A 314 Bedroom 2 | Pass | Pass | Pass
Block A 314 Bedroom 1 | Pass | Pass | Pass
Block A 314 LKD | Pass | NA | Pass
Block A 304 Bedroom 2 | Pass | Pass | Pass
Block A 304 Bedroom 1 | Pass | Pass | Pass
Block A 304 LKD | Pass | NA | Pass
Block A 309 Bedroom 1 | Pass | Pass | Pass
Block A 309 LKD | Pass | NA | Pass
Block A 514 Bedroom 2 | Pass | Pass | Pass
Block A 514 Bedroom 1 | Pass | Pass | Pass
Block A 514 LKD | Pass | NA | Pass
Block A 504 Bedroom 1 | Pass | Pass | Pass
Block A 504 Bedroom 2 | Pass | Pass | Pass
Block A 504 LKD | Pass | NA | Pass
Block A 509 Bedroom 1 | Pass | Pass | Pass
Block A 509 LKD | Pass | NA | Pass
Block A 309 Bedroom 2 | Pass | Pass | Pass
Block A 509 Bedroom 2 | Pass | Pass | Pass

## Natvent rooms criterion (a)
CIBSE TM59 Overheating assessment - Predominately nat vent rooms criterion (a)
Criterion (a) states that for living rooms, kitchens and bedrooms, the number of hours during which ΔT is greater than or equal to 1⁰K from May to September (or November to March for southern hemisphere locations) shall not exceed 3% of occupied hours.
Room Name | Occupied hours | No. hours ΔT ≥ 1⁰K | % Occupied hours ΔT ≥ 1⁰K | Pass/Fail
Block A 301 LKD | 1989 | 19 | 1 | Pass
Block A 301 Bedroom 1 | 3672 | 10 | 0.3 | Pass
Block A 301 Bedroom 2 | 3672 | 15 | 0.4 | Pass
Block A 302 LKD | 1989 | 16 | 0.8 | Pass
Block A 302 Bedroom 1 | 3672 | 10 | 0.3 | Pass
Block A 302 Bedroom 2 | 3672 | 8 | 0.2 | Pass
Block A 303 Bedroom | 3672 | 6 | 0.2 | Pass
Block A 303 LKD | 1989 | 7 | 0.4 | Pass
Block A 305 LKD | 1989 | 15 | 0.8 | Pass
Block A 305 Bedroom 1 | 3672 | 14 | 0.4 | Pass
Block A 305 Bedroom 2 | 3672 | 10 | 0.3 | Pass
Block A 305 Bedroom 3 | 3672 | 7 | 0.2 | Pass
Block A 306 Bedroom | 3672 | 4 | 0.1 | Pass
Block A 306 LKD | 1989 | 6 | 0.3 | Pass
Block A 307 Bedroom | 3672 | 3 | 0.1 | Pass
Block A 307 LKD | 1989 | 2 | 0.1 | Pass
Block A 308 LKD | 1989 | 4 | 0.2 | Pass
Block A 308 Bedroom | 3672 | 0 | 0 | Pass
Block A 310 Bedroom 1 | 3672 | 6 | 0.2 | Pass
Block A 310 Bedroom 2 | 3672 | 7 | 0.2 | Pass
Block A 310 LKD | 1989 | 17 | 0.9 | Pass
Block A 311 LKD | 1989 | 0 | 0 | Pass
Block A 311 Bedroom | 3672 | 16 | 0.4 | Pass
Block A 320 Bedroom | 3672 | 5 | 0.1 | Pass
Block A 320 LKD | 1989 | 8 | 0.4 | Pass
Block A 312 Bedroom 1 | 3672 | 17 | 0.5 | Pass
Block A 312 LKD | 1989 | 20 | 1 | Pass
Block A 312 Bedroom 2 | 3672 | 7 | 0.2 | Pass
Block A 313 LKD | 1989 | 7 | 0.4 | Pass
Block A 313 Bedroom | 3672 | 3 | 0.1 | Pass
Block A 315 Bedroom 1 | 3672 | 10 | 0.3 | Pass
Block A 315 Bedroom 2 | 3672 | 4 | 0.1 | Pass
Block A 315 LKD | 1989 | 8 | 0.4 | Pass
Block A 316 LKD | 1989 | 8 | 0.4 | Pass
Block A 316 Bedroom | 3672 | 5 | 0.1 | Pass
Block A 317 LKD | 1989 | 7 | 0.4 | Pass
Block A 317 Bedroom | 3672 | 4 | 0.1 | Pass
Block A 318 Bedroom 1 | 3672 | 6 | 0.2 | Pass
Block A 318 Bedroom 2 | 3672 | 8 | 0.2 | Pass
Block A 318 LKD | 1989 | 18 | 0.9 | Pass
Block A 319 Bedroom 1 | 3672 | 6 | 0.2 | Pass
Block A 319 Bedroom 2 | 3672 | 6 | 0.2 | Pass
Block A 319 LKD | 1989 | 15 | 0.8 | Pass
Block B 301 LKD | 1989 | 22 | 1.1 | Pass
Block B 301 Bedroom | 3672 | 9 | 0.2 | Pass
Block B 302 LKD | 1989 | 17 | 0.9 | Pass
Block B 302 Bedroom 1 | 3672 | 4 | 0.1 | Pass
Block B 302 Bedroom 2 | 3672 | 0 | 0 | Pass
Block B 303 LKD | 1989 | 20 | 1 | Pass
Block B 303 Bedroom 1 | 3672 | 0 | 0 | Pass
Block B 303 Bedroom 2 | 3672 | 4 | 0.1 | Pass
Block B 304 Bedroom | 3672 | 0 | 0 | Pass
Block B 306 Bedroom 1 | 3672 | 23 | 0.6 | Pass
Block B 306 Bedroom 2 | 3672 | 10 | 0.3 | Pass
Block B 306 LKD | 1989 | 23 | 1.2 | Pass
Block B 304 LKD | 1989 | 8 | 0.4 | Pass
Block B 305 Studio | 3672 | 7 | 0.2 | Pass
Block B 307 Bedroom | 3672 | 7 | 0.2 | Pass
Block B 307 LKD | 1989 | 19 | 1 | Pass
Block A 501 LKD | 1989 | 19 | 1 | Pass
Block A 501 Bedroom 1 | 3672 | 11 | 0.3 | Pass
Block A 501 Bedroom 2 | 3672 | 16 | 0.4 | Pass
Block A 502 LKD | 1989 | 16 | 0.8 | Pass
Block A 502 Bedroom 1 | 3672 | 11 | 0.3 | Pass
Block A 502 Bedroom 2 | 3672 | 10 | 0.3 | Pass
Block A 503 Bedroom | 3672 | 5 | 0.1 | Pass
Block A 503 LKD | 1989 | 9 | 0.5 | Pass
Block A 505 LKD | 1989 | 16 | 0.8 | Pass
Block A 505 Bedroom 1 | 3672 | 16 | 0.4 | Pass
Block A 505 Bedroom 2 | 3672 | 12 | 0.3 | Pass
Block A 505 Bedroom 3 | 3672 | 8 | 0.2 | Pass
Block A 506 Bedroom | 3672 | 4 | 0.1 | Pass
Block A 506 LKD | 1989 | 7 | 0.4 | Pass
Block A 507 Bedroom | 3672 | 4 | 0.1 | Pass
Block A 507 LKD | 1989 | 2 | 0.1 | Pass
Block A 508 LKD | 1989 | 5 | 0.3 | Pass
Block A 508 Bedroom | 3672 | 10 | 0.3 | Pass
Block A 515 Bedroom 1 | 3672 | 12 | 0.3 | Pass
Block A 515 Bedroom 2 | 3672 | 4 | 0.1 | Pass
Block A 516 LKD | 1989 | 10 | 0.5 | Pass
Block A 516 Bedroom | 3672 | 5 | 0.1 | Pass
Block A 517 LKD | 1989 | 7 | 0.4 | Pass
Block A 517 Bedroom | 3672 | 4 | 0.1 | Pass
Block A 518 Bedroom 1 | 3672 | 8 | 0.2 | Pass
Block A 518 Bedroom 2 | 3672 | 9 | 0.2 | Pass
Block A 518 LKD | 1989 | 19 | 1 | Pass
Block A 519 Bedroom 1 | 3672 | 6 | 0.2 | Pass
Block A 519 Bedroom 2 | 3672 | 7 | 0.2 | Pass
Block A 519 LKD | 1989 | 16 | 0.8 | Pass
Block B 501 LKD | 1989 | 22 | 1.1 | Pass
Block B 501 Bedroom | 3672 | 10 | 0.3 | Pass
Block B 502 LKD | 1989 | 18 | 0.9 | Pass
Block B 502 Bedroom 1 | 3672 | 4 | 0.1 | Pass
Block B 502 Bedroom 2 | 3672 | 1 | 0 | Pass
Block B 503 LKD | 1989 | 20 | 1 | Pass
Block B 503 Bedroom 1 | 3672 | 1 | 0 | Pass
Block B 503 Bedroom 2 | 3672 | 4 | 0.1 | Pass
Block B 504 Bedroom | 3672 | 0 | 0 | Pass
Block B 506 Bedroom 1 | 3672 | 23 | 0.6 | Pass
Block B 506 Bedroom 2 | 3672 | 10 | 0.3 | Pass
Block B 506 LKD | 1989 | 24 | 1.2 | Pass
Block B 504 LKD | 1989 | 8 | 0.4 | Pass
Block B 505 Studio | 3672 | 8 | 0.2 | Pass
Block B 507 Bedroom | 3672 | 8 | 0.2 | Pass
Block B 507 LKD | 1989 | 19 | 1 | Pass
Block A 515 LKD | 1989 | 20 | 1 | Pass
Block B 1101 LKD | 1989 | 24 | 1.2 | Pass
Block B 1101 Bedroom | 3672 | 12 | 0.3 | Pass
Block B 1102 LKD | 1989 | 23 | 1.2 | Pass
Block B 1102 Bedroom 1 | 3672 | 6 | 0.2 | Pass
Block B 1102 Bedroom 2 | 3672 | 4 | 0.1 | Pass
Block B 1103 LKD | 1989 | 20 | 1 | Pass
Block B 1103 Bedroom 1 | 3672 | 4 | 0.1 | Pass
Block B 1103 Bedroom 2 | 3672 | 4 | 0.1 | Pass
Block B 1104 Bedroom | 3672 | 0 | 0 | Pass
Block B 1106 Bedroom 1 | 3672 | 23 | 0.6 | Pass
Block B 1106 Bedroom 2 | 3672 | 10 | 0.3 | Pass
Block B 1106 LKD | 1989 | 24 | 1.2 | Pass
Block B 1104 LKD | 1989 | 9 | 0.5 | Pass
Block B 1105 Studio | 3672 | 10 | 0.3 | Pass
Block B 1107 Bedroom | 3672 | 8 | 0.2 | Pass
Block B 1107 LKD | 1989 | 19 | 1 | Pass
Block A 314 Bedroom 2 | 3672 | 9 | 0.2 | Pass
Block A 314 Bedroom 1 | 3672 | 9 | 0.2 | Pass
Block A 314 LKD | 1989 | 8 | 0.4 | Pass
Block A 304 Bedroom 2 | 3672 | 13 | 0.4 | Pass
Block A 304 Bedroom 1 | 3672 | 8 | 0.2 | Pass
Block A 304 LKD | 1989 | 17 | 0.9 | Pass
Block A 309 Bedroom 1 | 3672 | 7 | 0.2 | Pass
Block A 309 LKD | 1989 | 7 | 0.4 | Pass
Block A 514 Bedroom 2 | 3672 | 15 | 0.4 | Pass
Block A 514 Bedroom 1 | 3672 | 8 | 0.2 | Pass
Block A 514 LKD | 1989 | 19 | 1 | Pass
Block A 504 Bedroom 1 | 3672 | 9 | 0.2 | Pass
Block A 504 Bedroom 2 | 3672 | 14 | 0.4 | Pass
Block A 504 LKD | 1989 | 18 | 0.9 | Pass
Block A 509 Bedroom 1 | 3672 | 9 | 0.2 | Pass
Block A 509 LKD | 1989 | 20 | 1 | Pass
Block A 309 Bedroom 2 | 3672 | 7 | 0.2 | Pass
Block A 509 Bedroom 2 | 3672 | 9 | 0.2 | Pass

## Natvent rooms criterion (b)
CIBSE TM59 Overheating assessment - Predominately nat vent rooms criterion (b)
Criterion (b) states that the operative temperature of the bedrooms from 22:00-07:00 shall not exceed 26⁰C for more than 1% of annual hours (33 hours is therefore recorded as a fail).
Any rooms that are not bedrooms are therefore not assessed, hence the corresponding NA values.
Room Name | No. hours > 26⁰C 22:00-24:00 | No. hours > 26⁰C 00:00-07:00 | Total hours > 26⁰C | Pass/Fail
Block A 301 LKD | NA | NA | NA | NA
Block A 301 Bedroom 1 | 6 | 0 | 6 | Pass
Block A 301 Bedroom 2 | 4 | 0 | 4 | Pass
Block A 302 LKD | NA | NA | NA | NA
Block A 302 Bedroom 1 | 3 | 0 | 3 | Pass
Block A 302 Bedroom 2 | 8 | 0 | 8 | Pass
Block A 303 Bedroom | 3 | 0 | 3 | Pass
Block A 303 LKD | NA | NA | NA | NA
Block A 305 LKD | NA | NA | NA | NA
Block A 305 Bedroom 1 | 12 | 5 | 17 | Pass
Block A 305 Bedroom 2 | 4 | 0 | 4 | Pass
Block A 305 Bedroom 3 | 3 | 0 | 3 | Pass
Block A 306 Bedroom | 1 | 0 | 1 | Pass
Block A 306 LKD | NA | NA | NA | NA
Block A 307 Bedroom | 1 | 0 | 1 | Pass
Block A 307 LKD | NA | NA | NA | NA
Block A 308 LKD | NA | NA | NA | NA
Block A 308 Bedroom | 1 | 0 | 1 | Pass
Block A 310 Bedroom 1 | 1 | 0 | 1 | Pass
Block A 310 Bedroom 2 | 2 | 0 | 2 | Pass
Block A 310 LKD | NA | NA | NA | NA
Block A 311 LKD | NA | NA | NA | NA
Block A 311 Bedroom | 2 | 0 | 2 | Pass
Block A 320 Bedroom | 1 | 0 | 1 | Pass
Block A 320 LKD | NA | NA | NA | NA
Block A 312 Bedroom 1 | 4 | 0 | 4 | Pass
Block A 312 LKD | NA | NA | NA | NA
Block A 312 Bedroom 2 | 2 | 0 | 2 | Pass
Block A 313 LKD | NA | NA | NA | NA
Block A 313 Bedroom | 1 | 0 | 1 | Pass
Block A 315 Bedroom 1 | 11 | 1 | 12 | Pass
Block A 315 Bedroom 2 | 3 | 0 | 3 | Pass
Block A 315 LKD | NA | NA | NA | NA
Block A 316 LKD | NA | NA | NA | NA
Block A 316 Bedroom | 1 | 0 | 1 | Pass
Block A 317 LKD | NA | NA | NA | NA
Block A 317 Bedroom | 1 | 0 | 1 | Pass
Block A 318 Bedroom 1 | 2 | 0 | 2 | Pass
Block A 318 Bedroom 2 | 2 | 0 | 2 | Pass
Block A 318 LKD | NA | NA | NA | NA
Block A 319 Bedroom 1 | 2 | 0 | 2 | Pass
Block A 319 Bedroom 2 | 2 | 0 | 2 | Pass
Block A 319 LKD | NA | NA | NA | NA
Block B 301 LKD | NA | NA | NA | NA
Block B 301 Bedroom | 2 | 0 | 2 | Pass
Block B 302 LKD | NA | NA | NA | NA
Block B 302 Bedroom 1 | 2 | 0 | 2 | Pass
Block B 302 Bedroom 2 | 2 | 0 | 2 | Pass
Block B 303 LKD | NA | NA | NA | NA
Block B 303 Bedroom 1 | 2 | 0 | 2 | Pass
Block B 303 Bedroom 2 | 2 | 0 | 2 | Pass
Block B 304 Bedroom | 0 | 0 | 0 | Pass
Block B 306 Bedroom 1 | 13 | 3 | 16 | Pass
Block B 306 Bedroom 2 | 2 | 0 | 2 | Pass
Block B 306 LKD | NA | NA | NA | NA
Block B 304 LKD | NA | NA | NA | NA
Block B 305 Studio | 2 | 0 | 2 | Pass
Block B 307 Bedroom | 2 | 0 | 2 | Pass
Block B 307 LKD | NA | NA | NA | NA
Block A 501 LKD | NA | NA | NA | NA
Block A 501 Bedroom 1 | 6 | 0 | 6 | Pass
Block A 501 Bedroom 2 | 4 | 0 | 4 | Pass
Block A 502 LKD | NA | NA | NA | NA
Block A 502 Bedroom 1 | 3 | 0 | 3 | Pass
Block A 502 Bedroom 2 | 8 | 0 | 8 | Pass
Block A 503 Bedroom | 2 | 0 | 2 | Pass
Block A 503 LKD | NA | NA | NA | NA
Block A 505 LKD | NA | NA | NA | NA
Block A 505 Bedroom 1 | 12 | 6 | 18 | Pass
Block A 505 Bedroom 2 | 4 | 0 | 4 | Pass
Block A 505 Bedroom 3 | 3 | 0 | 3 | Pass
Block A 506 Bedroom | 1 | 0 | 1 | Pass
Block A 506 LKD | NA | NA | NA | NA
Block A 507 Bedroom | 1 | 0 | 1 | Pass
Block A 507 LKD | NA | NA | NA | NA
Block A 508 LKD | NA | NA | NA | NA
Block A 508 Bedroom | 2 | 0 | 2 | Pass
Block A 515 Bedroom 1 | 11 | 1 | 12 | Pass
Block A 515 Bedroom 2 | 3 | 0 | 3 | Pass
Block A 516 LKD | NA | NA | NA | NA
Block A 516 Bedroom | 1 | 0 | 1 | Pass
Block A 517 LKD | NA | NA | NA | NA
Block A 517 Bedroom | 1 | 0 | 1 | Pass
Block A 518 Bedroom 1 | 2 | 0 | 2 | Pass
Block A 518 Bedroom 2 | 2 | 0 | 2 | Pass
Block A 518 LKD | NA | NA | NA | NA
Block A 519 Bedroom 1 | 1 | 0 | 1 | Pass
Block A 519 Bedroom 2 | 2 | 0 | 2 | Pass
Block A 519 LKD | NA | NA | NA | NA
Block B 501 LKD | NA | NA | NA | NA
Block B 501 Bedroom | 2 | 0 | 2 | Pass
Block B 502 LKD | NA | NA | NA | NA
Block B 502 Bedroom 1 | 2 | 0 | 2 | Pass
Block B 502 Bedroom 2 | 2 | 0 | 2 | Pass
Block B 503 LKD | NA | NA | NA | NA
Block B 503 Bedroom 1 | 2 | 0 | 2 | Pass
Block B 503 Bedroom 2 | 2 | 0 | 2 | Pass
Block B 504 Bedroom | 1 | 0 | 1 | Pass
Block B 506 Bedroom 1 | 13 | 2 | 15 | Pass
Block B 506 Bedroom 2 | 2 | 0 | 2 | Pass
Block B 506 LKD | NA | NA | NA | NA
Block B 504 LKD | NA | NA | NA | NA
Block B 505 Studio | 2 | 0 | 2 | Pass
Block B 507 Bedroom | 2 | 0 | 2 | Pass
Block B 507 LKD | NA | NA | NA | NA
Block A 515 LKD | NA | NA | NA | NA
Block B 1101 LKD | NA | NA | NA | NA
Block B 1101 Bedroom | 2 | 0 | 2 | Pass
Block B 1102 LKD | NA | NA | NA | NA
Block B 1102 Bedroom 1 | 3 | 0 | 3 | Pass
Block B 1102 Bedroom 2 | 3 | 0 | 3 | Pass
Block B 1103 LKD | NA | NA | NA | NA
Block B 1103 Bedroom 1 | 3 | 0 | 3 | Pass
Block B 1103 Bedroom 2 | 3 | 0 | 3 | Pass
Block B 1104 Bedroom | 1 | 0 | 1 | Pass
Block B 1106 Bedroom 1 | 12 | 2 | 14 | Pass
Block B 1106 Bedroom 2 | 2 | 0 | 2 | Pass
Block B 1106 LKD | NA | NA | NA | NA
Block B 1104 LKD | NA | NA | NA | NA
Block B 1105 Studio | 2 | 0 | 2 | Pass
Block B 1107 Bedroom | 2 | 0 | 2 | Pass
Block B 1107 LKD | NA | NA | NA | NA
Block A 314 Bedroom 2 | 2 | 0 | 2 | Pass
Block A 314 Bedroom 1 | 2 | 0 | 2 | Pass
Block A 314 LKD | NA | NA | NA | NA
Block A 304 Bedroom 2 | 3 | 0 | 3 | Pass
Block A 304 Bedroom 1 | 3 | 0 | 3 | Pass
Block A 304 LKD | NA | NA | NA | NA
Block A 309 Bedroom 1 | 3 | 0 | 3 | Pass
Block A 309 LKD | NA | NA | NA | NA
Block A 514 Bedroom 2 | 3 | 0 | 3 | Pass
Block A 514 Bedroom 1 | 6 | 0 | 6 | Pass
Block A 514 LKD | NA | NA | NA | NA
Block A 504 Bedroom 1 | 3 | 0 | 3 | Pass
Block A 504 Bedroom 2 | 3 | 0 | 3 | Pass
Block A 504 LKD | NA | NA | NA | NA
Block A 509 Bedroom 1 | 3 | 0 | 3 | Pass
Block A 509 LKD | NA | NA | NA | NA
Block A 309 Bedroom 2 | 2 | 0 | 2 | Pass
Block A 509 Bedroom 2 | 3 | 0 | 3 | Pass

## Mechvent rooms
CIBSE TM59 Overheating assessment - Predominately mech vent rooms
CIBSE TM59 overheating methodology for predominately mech vent rooms states the operative temperature of all rooms shall not exceed 26⁰C for more than 3% of annual occupied hours.
Room name | No. hours > 26⁰C | % Annual hours > 26⁰C | Pass/Fail
No mech vent rooms to be analysed | NA | NA | NA

## Communal corridors
CIBSE TM59 Overheating assessment - Communal corridors
TM59 states that whilst there is no mandatory target for communal corridors, if an operative temperature of 28⁰C is exceeded for more than 3% of the total annual hours,
then this should be identified as a significant risk within the TM59 overheating report.
Corridor name | No. hours > 28⁰C | % Annual hours > 28⁰C | Significant overheating risk?
Block A L3 Corridor 1 | 3660 | 41.8 | Yes
Block A L3 Lobby 1 | 8760 | 100 | Yes
Block A L3 Lobby 2 | 8760 | 100 | Yes
Block A L3 Lobby 3 | 4331 | 49.4 | Yes
Block A L3 Corridor 3 | 334 | 3.8 | Yes
Block A L3 Corridor 5 | 2587 | 29.5 | Yes
Block A L3 Lobby 4 | 8421 | 96.1 | Yes
Block A L3 Lobby 5 | 8760 | 100 | Yes
Block B L3 Lobby 1 | 8760 | 100 | Yes
Block B L3 Lobby 2 | 8760 | 100 | Yes
Block B L3 Corridor 2 | 7793 | 89 | Yes
Block B L3 Corridor 1 | 4787 | 54.6 | Yes
Block A L5 Corridor 1 | 3487 | 39.8 | Yes
Block A L5 Lobby 1 | 8760 | 100 | Yes
Block A L5 Lobby 2 | 8760 | 100 | Yes
Block A L5 Corridor 5 | 2741 | 31.3 | Yes
Block A L5 Lobby 4 | 8760 | 100 | Yes
Block A L5 Lobby 5 | 8760 | 100 | Yes
Block B L5 Lobby 1 | 8760 | 100 | Yes
Block B L5 Lobby 2 | 8760 | 100 | Yes
Block B L5 Corridor 2 | 7800 | 89 | Yes
Block B L5 Corridor 1 | 4814 | 55 | Yes
Block B L11 Lobby 1 | 8760 | 100 | Yes
Block B L11 Lobby 2 | 8760 | 100 | Yes
Block B L11 Corridor 2 | 7274 | 83 | Yes
Block B L11 Corridor 1 | 4524 | 51.6 | Yes
Block A L3 Corridor 2 | 1597 | 18.2 | Yes